## Sheet1
Section | Item | Vendor 1 | Vendor 2 | Vendor 3 | Buyer Check | Red Flag
Basic Requirement | Crane capacity and quantity |  |  |  | Confirm all cranes sharing the bay are listed | Vendor assumes only one crane current
Basic Requirement | Runway length / DSL length |  |  |  | Use actual bay travel length in meters | Length missing or rounded down
Basic Requirement | Feed arrangement |  |  |  | End feed / center feed / dual end feed / multiple feed points | Vendor says standard without layout
Electrical Rating | Current per crane |  |  |  | Ask for current of each crane not only total connected load | One average current used for different cranes
Electrical Rating | Simultaneity factor |  |  |  | Confirm how many cranes can run together at peak load | No basis for diversity factor
Electrical Rating | Busbar current rating |  |  |  | Compare design current against offered busbar rating | Rating lower than design current
Electrical Rating | Voltage drop calculation |  |  |  | Ask vendor to submit calculation with conductor data | Voltage drop not checked
Electrical Rating | Conductor material |  |  |  | Copper / aluminium / galvanized steel conductor details | Material not declared
Busbar Supply | Busbar make and model |  |  |  | Record brand and exact series offered | Only generic busbar mentioned
Busbar Supply | Number of poles / conductors |  |  |  | Check phase neutral earth control requirement | Poles not matching application
Busbar Supply | Insulating housing / shrouding |  |  |  | Check finger-safe shrouded construction | Open conductor offered for normal indoor bay
Busbar Supply | IP rating / environment suitability |  |  |  | Check dust heat humidity outdoor exposure | No environment suitability statement
Busbar Supply | Expansion joints |  |  |  | Required for long runs or temperature variation | No expansion provision on long bay
Busbar Supply | Joint kits and covers |  |  |  | Check included quantity and joint protection | Joints excluded or unclear
Busbar Supply | Hangers / brackets |  |  |  | Check spacing and structural fixing scope | Supports excluded from quote
Collectors | Collector current rating |  |  |  | Rating should suit crane current and duty | Collector rating lower than operating load
Collectors | Number of collector shoes |  |  |  | Ask if spare shoes / twin collectors needed | Single collector for high duty application
Collectors | Collector make and spare availability |  |  |  | Check local availability and replacement cost | Unknown make with no spare support
Feed & Protection | End feed / power feed box |  |  |  | Check included with cable glands and terminals | Feed box excluded
Feed & Protection | Isolator / switch disconnector |  |  |  | Clarify scope between buyer and vendor | Isolation not included anywhere
Feed & Protection | Earthing arrangement |  |  |  | Confirm earth conductor and bonding | Earth path assumed through structure only
Installation | Installation scope |  |  |  | Supply only / supervision / installation / commissioning | Scope boundary unclear
Installation | Alignment and commissioning checks |  |  |  | Ask for collector tracking and joint inspection procedure | No commissioning checklist
Testing | FAT/SAT checks |  |  |  | Confirm insulation resistance continuity trial run and voltage checks | No acceptance criteria stated
Spares | Recommended spares |  |  |  | Collector shoes joint covers end caps fuses | No spares list
Commercial | Warranty |  |  |  | Check warranty on busbar collectors and installation | Consumables excluded without clarity
Commercial | Documentation |  |  |  | Ask for GA layout voltage drop calculation datasheet and manual | No documentation commitment